(TTO-13464-03)

电气参数Electronical characteristics

| 产品型号 Production model | (TTO-13464-03) |
| --- | --- |
| 额定输出功率 Rated output power | AC 230VA (Max) |
| 初级额定电压 Primary Rated voltage | AC 230V |
| 额定频率 Rated ferquency | 50Hz |
| 次级空载电压 Secondary no-load voltage | AC 34.6V Max |
| 次级负载电压/电流 Secondary loaded voltage / current | AC 30V±5% @ 11.33A(ED10%) 15V±5% @ 0.3A (RD100%) |
| 初级空载电流 Primary exciting current | Max. 60mA(初级额定输入电压Primary rated input voltage) |
| 安全标准 Safety standard | UL 60601-1 绝缘系统( UL60601-1 insulation system) CE |
| 绝缘等级 Insulation class | Class B (130Deg.C) |
| 接地系统Ground system | Class-II |
| 温升Temperature rise | 85Deg.C Max.(额定输入at reted input) |
| 外施耐压试验Dielectric Withstand Test | AC 4000V 5mA 1 分钟Minute(初级对次级Primary to Secondary) |
| 感应耐压试验Induced withstand voltage test | AC 460V 400Hz 15S(初级Primary ) |
| 绝缘电阻试验Measurement of dry insulation-resistance | 100M OHM @ DC 500V |
| 安装尺寸Installation size |  |

附项选择 additional item

| 温度保护 Thermal Protector | SM1 110摄氏度温度開關保险SM1 110Deg.C Thermal switch |
| --- | --- |
| 短路保护 Short-circuit Protector | 无No，但可根据客户要求增加No,but can increase according to customer’s requirement. |
| 五金配件 Hardware accessories | 铁盘子Steel dished washer：Φ6.5x68mm 1个 橡胶垫Neoprene washer： Φ6.5x68mm 2个 平垫圈Flat washer： ****** 弹簧垫圈Spring washer： ****** 螺丝Hex secews: M6x65mm 1个 螺母Nut: M6 1个 |
| 静电屏蔽 Electronic shielding | 无No，但可根据客户要求增加No,but can increase according to customer’s requirement. |
| 电磁屏蔽 Magnetic shielding | 无No，但可根据客户要求增加No,but can increase according to customer’s requirement. |
| 中心孔灌环氧树脂 Filled epoxy resin | 无No，但可根据客户要求增加No,but can increase according to customer’s requirement. |